## PAR Template
PRE-APPLICATION REPORT
Prepared By: | <Cooperative Name>
Prepared For: | <Requester Name>
Date Prepared: | <Date>
LIKELY POINT OF INTERCONNECTION (POI) INFORMATION
LOCATION IDENTIFIED BASED ON INFORMATION SUPPLIED ON THE PAR REQUEST FORM
Substation:
Circuit:
Line Section / Map Number:
Substation Nominal Distribution Voltage (kV): |  |  | Phase-phase and phase-ground (e.g. 12.47/7.2 =
12.47kV phase-phase and 7.2kV phase-ground)
Nominal Distribution Voltage at POI (kV): |  |  | Phase-phase and phase-ground (e.g. 12.47/7.2 =
12.47kV phase-phase and 7.2kV phase-ground)
POI Distance from Substation (circuit miles):
Number of Phases Available at POI: |  |  | This number represents the number of primary
distribution phases available at the POI
Distance from three-phase if applicable (miles): |  |  | This estimate may change based on the actual
line design to extend three-phase to the POI
Configuration of Cooperative System at POI: |  |  | "Spot Network" - secondary network
"Grid Network" - two or more distribution sources
"Radial Supply" - only one distribution source
CAPACITIES
| (1) | (2) | (3) | (4)
| Total | Existing Interconnected | Aggregate Generation | Available
System | Capacity | Aggregate Generation | Queued Capacity | Capacity
Level | (MW) | Capacity (MW) | (MW) | (MW)
Substation |  |  |  | 0
Circuit |  |  |  | 0
Column Descriptions:
(1) Total capacity in MW of the system level component. Capacity value based on most limiting component
(e.g. transformer, conductors, switches, connectors, etc).
(2) Total aggregate installed nameplate generation capacity in MW interconnected on the system level
component.
(3) Total aggregate nameplate generation capacity in MW of all interconnection applications received and in
queue on the system level component.
(4) Available capacity calculated as column (1) less the sum of columns (2) and (3). Available capacity does not
imply that an interconnection up to this level may be completed without any adverse system impacts since
there are many variables studies as part of the interconnection review process.
LINE SECTION LOAD INFORMATION
A line section is that portion of the Cooperative's electric system connected to a customer bounded
by automatic sectionalizing devices or the end of the distribution line.
(1) | (2) | (3)
Load Type | Load (MW) | Estimated or Actual
Peak
Absolute Minimum
Daytime Minimum
Column Descriptions:
(1) "Peak" is defined as the highest load at any time period. "Absolute Minimum" is defined as the lowest load at any
time period. "Daytime Minimum" is defined as the minimum load during the hours of 10 a.m. to 4 p.m.
Any load data that is not readily available is indicated as such.
(2) Line Section Load in MW.
(3) The load values included in column (2) are indicated to be either "Estimated" or "Actual" measured values.
PROTECTIVE AND VOLTAGE REGULATING DEVICES
The following lists existing protective and voltage regulating devices installed
between the Cooperative substation and the identified POI.
PROTECTIVE DEVICES
(1) | (2) | (3) | (4)
Device | Rating (Amps) | Bi-Directional | Additional
|  | Operation Ok? | Notes
Column Descriptions:
(1) Indicates the protective device type and description.
(2) Indicates the protective device rating (in Amps).
(3) Indicates whether the protective device and its control, as applicable, can properly function in
bi-directional modes of operation with no adverse impacts or loss of protective functionality.
VOLTAGE REGULATING DEVICES
(1) | (2) | (3) | (4)
Device | Rating (Amps) | Bi-Directional | Additional
|  | Operation Ok? | Notes
Column Descriptions:
(1) Indicates the voltage regulating device type and description.
(2) Indicates the voltage regulating device rating (in Amps).
(3) Indicates whether the voltage regulating device and its control, as applicable, can properly
function in bi-directional modes of operation with no adverse impacts to system voltage levels.
NOTE: Any Load Tap Changer (LTC) devices installed at the substation are included in the above list.
EXISTING OR KNOWN CONSTRAINTS
Listing of any existing or known constraints such as, but not limited to, electrical dependencies at the POI, short circuit
interrupting capacity issues, power quality or stability issues on the circuit, capacity constraints, or secondary networks.
<List any constraints, or indicate "No known constraints">
ALL INFORMATION INCLUDED IN THIS REPORT REPRESENTS THE BEST AVAILABLE INFORMATION
AT THE TIME OF REPORTING. CONTINUED ACCURACY OF INFORMATION CANNOT BE GUARANTEED
AS DATA MAY BECOME OUTDATED BETWEEN THE TIME OF REPORTING AND THE ACTUAL
INTERCONNECTION APPLICATION BEING RECEIVED.

## PAR Example
PRE-APPLICATION REPORT
Prepared By: | XYZ Cooperative
Prepared For: | 123 Solar
Date Prepared: | 2014-07-02
LIKELY POINT OF INTERCONNECTION (POI) INFORMATION
LOCATION IDENTIFIED BASED ON INFORMATION SUPPLIED ON THE PAR REQUEST FORM
Substation: |  | Smith Road Substation
Circuit: |  | Circuit 3
Line Section / Map Number: |  | Line Section 195
Substation Nominal Distribution Voltage (kV): |  | 12.47/7.2 | Phase-phase and phase-ground (e.g. 12.47/7.2 =
12.47kV phase-phase and 7.2kV phase-ground)
Nominal Distribution Voltage at POI (kV): |  | 12.47/7.2 | Phase-phase and phase-ground (e.g. 12.47/7.2 =
12.47kV phase-phase and 7.2kV phase-ground)
POI Distance from Substation (circuit miles): |  | 5.6
Number of Phases Available at POI: |  | 1 | This number represents the number of primary
distribution phases available at the POI
Distance from three-phase if applicable (miles): |  | 1.5 | This estimate may change based on the actual
line design to extend three-phase to the POI
Configuration of Cooperative System at POI: |  | Radial Supply | "Spot Network" - secondary network
"Grid Network" - two or more distribution sources
"Radial Supply" - only one distribution source
CAPACITIES
| (1) | (2) | (3) | (4)
| Total | Existing Interconnected | Aggregate Generation | Available
System | Capacity | Aggregate Generation | Queued Capacity | Capacity
Level | (MW) | Capacity (MW) | (MW) | (MW)
Substation | 10 | 0.5 | 0 | 9.5
Circuit | 4.5 | 0.5 | 0 | 4
Column Descriptions:
(1) Total capacity in MW of the system level component. Capacity value based on most limiting component
(e.g. transformer, conductors, switches, connectors, etc).
(2) Total aggregate installed nameplate generation capacity in MW interconnected on the system level
component.
(3) Total aggregate nameplate generation capacity in MW of all interconnection applications received and in
queue on the system level component.
(4) Available capacity calculated as column (1) less the sum of columns (2) and (3). Available capacity does not
imply that an interconnection up to this level may be completed without any adverse system impacts since
there are many variables studies as part of the interconnection review process.
LINE SECTION LOAD INFORMATION
A line section is that portion of the Cooperative's electric system connected to a customer bounded
by automatic sectionalizing devices or the end of the distribution line.
(1) | (2) | (3)
Load Type | Load (MW) | Estimated or Actual
Peak | 0.2 | Estimated
Absolute Minimum | 0.07 | Estimated
Daytime Minimum | Not readily available
Column Descriptions:
(1) "Peak" is defined as the highest load at any time period. "Absolute Minimum" is defined as the lowest load at any
time period. "Daytime Minimum" is defined as the minimum load during the hours of 10 a.m. to 4 p.m.
Any load data that is not readily available is indicated as such.
(2) Line Section Load in MW.
(3) The load values included in column (2) are indicated to be either "Estimated" or "Actual" measured values.
PROTECTIVE AND VOLTAGE REGULATING DEVICES
The following lists existing protective and voltage regulating devices installed
between the Cooperative substation and the identified POI.
PROTECTIVE DEVICES
(1) | (2) | (3) | (4)
Device | Rating (Amps) | Bi-Directional | Additional
|  | Operation Ok? | Notes
Nova / Form 6 Control | 630 | No | PTs would need to be added to directionalize
50-L OCR | 50 | Yes | As long as DG fault contribution < 100A
Column Descriptions:
(1) Indicates the protective device type and description.
(2) Indicates the protective device rating (in Amps).
(3) Indicates whether the protective device and its control, as applicable, can properly function in
bi-directional modes of operation with no adverse impacts or loss of protective functionality.
VOLTAGE REGULATING DEVICES
(1) | (2) | (3) | (4)
Device | Rating (Amps) | Bi-Directional | Additional
|  | Operation Ok? | Notes
Regulators / CL-6 Control | 438 | Yes | Control has "Co-generation" mode available
Column Descriptions:
(1) Indicates the voltage regulating device type and description.
(2) Indicates the voltage regulating device rating (in Amps).
(3) Indicates whether the voltage regulating device and its control, as applicable, can properly
function in bi-directional modes of operation with no adverse impacts to system voltage levels.
NOTE: Any Load Tap Changer (LTC) devices installed at the substation are included in the above list.
EXISTING OR KNOWN CONSTRAINTS
Listing of any existing or known constraints such as, but not limited to, electrical dependencies at the POI, short circuit
interrupting capacity issues, power quality or stability issues on the circuit, capacity constraints, or secondary networks.
<List any constraints, or indicate "No known constraints">
ALL INFORMATION INCLUDED IN THIS REPORT REPRESENTS THE BEST AVAILABLE INFORMATION
AT THE TIME OF REPORTING. CONTINUED ACCURACY OF INFORMATION CANNOT BE GUARANTEED
AS DATA MAY BECOME OUTDATED BETWEEN THE TIME OF REPORTING AND THE ACTUAL
INTERCONNECTION APPLICATION BEING RECEIVED.