## Sheet1
Sample PV Solar Array |  |  | By: | PSE
Inspection, Testing and Commissioning Procedures* |  |  | Date: | 2013-05-23
|  | TEST | EXPECTED | PASS /
ITEM | TEST ACTIVITY | RESPONSIBILITY | RESULT | FAIL | WITNESS | NOTES
PRE-TEST CONDITIONS
1.1 | Conduct on-site job briefing to discuss the planned actions | ALL | All personnel briefed &
| and their sequences, known hazards, personal protection | PERSONNEL | signed-off
equipment, etc.
1.2 | Ensure PV array is disconnected and/or not operating | PSE/Cooperative | PV array disconnected
INSPECTION PROCEDURES
NOTE: | These inspection procedures are not intended to relieve the Interconnection Customer from complying with all
local and other applicable inspection requirements imposed by any duly-constituted regulatory authority .
2.1 | Verify local inspector requirements have been met | PSE/Cooperative | Compliance with local
| (documentation to be supplied by the interconnecting customer) |  | inspection requirements
2.2 | Inspect utility service to the residence. Note transformer size. | PSE/Cooperative | Compliance with NESC
Adequately sized transformer
2.3 | Inspect Interconnecting Customer's installation and facilities to | PSE/Cooperative | All installed facilities
| ensure what has been installed in the field matches the | Interconnecting | match supplied
| documentation supplied to the utility. | Customer | documentation
a. Inspect PV panel array and wiring (if readily accessible)
b. Inspect inverters (if readily accessible) and record any
status lights or display messages
1. Status Lights
2. Display messages
3. Other
c. Inspect residence main service panel and note circuit
PV array is feeding into and rating of overcurrent
protective device
d. Inspect sub-panel from PV Array and note circuit(s)
PV array is feeding into and rating of overcurrent
protective device
e. Inspect all grounding
f. Inspect AC disconnects, record ratings and verify operability
2.4 | Review programmed inverter field-adjustable voltage and frequency | PSE/Cooperative | Settings compliant |  |  |  |  | Clearing
| trip points and confirm compliance with IEEE Std. 1547 |  | with IEEE Std. 1547 |  |  | % | V / F | Time (sec)
| a. Overvoltage #1 setting and trip time |  |  |  |  | 120% | 288 | 0.16
| b. Overvoltage #2 setting and trip time |  |  |  |  | 110% | 264 | 1
| c. Undervoltage #1 setting and trip time |  |  |  |  | 88% | 211.2 | 2
| d. Undervoltage #2 setting and trip time |  |  |  |  | 50% | 120 | 0.16
| e. Overfrequency #1 setting and trip time |  |  |  |  | - | 60.5 | 0.16
| f. Underfrequency #1 setting and trip time |  |  |  |  | - | 59.8 | 0.16 - 300 | adjustable
| g. Underfrequency #2 setting and trip time |  |  |  |  | - | 57 | 0.16
TESTING PROCEDURES
3.1 | Verify PV array is disconnected and/or not operating | PSE/Cooperative | PV array disconnected
3.2 | Measure and record voltage at the meter, main panel and the PV | PSE/Cooperative | 120/240V Service
sub-panel with the PV array disconnected and/or not operating
a. Voltage measured at meter
| 1. L1 to L2 |  | Range of 228 - 252 Volts
| 2. L1 to Neutral |  | Range of 114 - 126 Volts
| 3. L2 to Neutral |  | Range of 114 - 126 Volts
b. Voltage measured at main panel
| 1. L1 to L2 |  | Range of 220 - 252 Volts
| 2. L1 to Neutral |  | Range of 110 - 126 Volts
| 3. L2 to Neutral |  | Range of 110 - 126 Volts
c. Voltage measured at PV sub-panel
| 1. L1 to L2 |  | Range of 220 - 252 Volts
| 2. L1 to Neutral |  | Range of 110 - 126 Volts
| 3. L2 to Neutral |  | Range of 110 - 126 Volts
3.3 | Establish AC voltage to the PV array and record time until the | PSE/Cooperative | Minimum 5 minute |  |  | Connect an Ammeter in the PV AC circuit(s)
| inverters begin outputting power. |  | delay before inverters
| Connect an ammeter in the PV AC circuit(s) to determine |  | output power
when the inverters begin outputting power
3.4 | Measure and record voltage at the meter, main panel and the | PSE/Cooperative | 120/240V Service
PV sub-panel with the PV array outputting power
a. Voltage measured at meter
| 1. L1 to L2 |  | Range of 228 - 252 Volts
| 2. L1 to Neutral |  | Range of 114 - 126 Volts
| 3. L2 to Neutral |  | Range of 114 - 126 Volts
b. Voltage measured at main panel
| 1. L1 to L2 |  | Range of 220 - 252 Volts
| 2. L1 to Neutral |  | Range of 110 - 126 Volts
| 3. L2 to Neutral |  | Range of 110 - 126 Volts
c. Voltage measured at PV sub-panel
| 1. L1 to L2 |  | Range of 220 - 252 Volts
| 2. L1 to Neutral |  | Range of 110 - 126 Volts
| 3. L2 to Neutral |  | Range of 110 - 126 Volts
3.5 | Measure and record amperage in each PV AC circuit | PSE/Cooperative | Current up to the
| a. Amperage measured at main service panel |  | rated capacity present
b. Amperage measured at PV sub-panel
3.6 | Optional for inverters certified to meet UL 1741: |  | Compliance with
IEEE Std. 1547
| a. Measure and record individual current harmonics and | PSE/Cooperative
total harmonic distortion
| b. Measure and record DC component (frequency < 1 Hz) | PSE/Cooperative
of current
| c. Require interconnecting customer to perform field tests | Interconnecting
| verifying over/under voltage and frequency trip points | Customer
and times.
3.7 | Conduct a "cease-to-energize" test | PSE/Cooperative | Compliance with
| Connect an ammeter in the PV AC circuit(s) to determine |  | IEEE Std. 1547
when the inverters stop/begin outputting power
a. Verify PV array is operating and connected in parallel
with utility source.
b. Remove utility source by opening a main breaker or
opening a fuse. Ideally the device used to disconnect the
utility source will still allow the residence loads to be
connected on the PV array side of the open.
| c. Record the time for the PV array and inverters to |  | Output ceases within |  |  | Connect an Ammeter in the PV AC circuit(s)
| automatically stop outputting power. |  | 2 seconds
d. Observe the status of the inverters and record any status
lights or display messages
1. Status Lights
2. Display messages
3. Other
| e. Re-establish AC voltage to the PV array and record time |  | Minimum 5 minute |  |  | Connect an Ammeter in the PV AC circuit(s)
| until the inverters begin outputting power again. |  | delay before inverters
output power
COMMENTS
WITNESSED BY: |  |  |  | DATE:
: Cooperative
: Cooperative
: Cooperative
: Power System Engineering
: Interconnecting Customer
: __________________
: __________________
: __________________
*DISCLAIMER
Utility's observation, review, inspection or testing shall be construed neither as an endorsement or confirmation of any aspect,
feature, element, or condition of the Generation Facility or Interconnection Customer's protective equipment or the operation
thereof, nor as a warranty as to the fitness, safety, desirability, or reliability of same.