## Energy
PV Solar Site
Energy Performance Test
Site Name:
System Designation: |  |  | Type of Inspection:
Inspection Date: |  |  | Commissioned Date:
Readings between 9:00 and 15:00 Total of Draker 15 Minute Time Weighted Averages)
Module Manufacturer
Model Number
Normal Operating Cell Temperature NOCT (800W/m2 and 45.7oC)
| Power Output @ NOCT = (PNOTC) |  |  | Watts
| Power Temp. Coef. = (PMPP) |  |  | %/oC
| Total Number of Modules |  |  | Modules
System Peak DC Energy = (EMAX)
| (EMAX) = (PNOTC) x (# of Mod) x 6 Hrs./1000 = |  |  | 0 |  | KWh
System De-rating Factor = (KS)
| Module mismatch |  | 0.97
| Inverter efficiency |  | 0.96
| Module soiling |  | 1
| Module nameplate tolerance |  | 0.99
| Wiring losses |  | 0.98
| Shading |  | 1
| System availability |  | 1
| Tacking efficiency |  | 1
| Age |  | 1
|  |  |  | (KS)= the product of all of the above factors = | 0.90345
Actual Irradiance during the test |  |  |  | Wh/m2 |  | > 4.2 KWh/m2 or 700W/m2
Actual Module Temperature during the test |  |  |  | o C
Irradiance Factor = (KI)
|  | (KI) = Actual Insolation / 4.8 KWh/m2 = | 0
Module Cell Temperature Facture = (KT)
|  | (KT) = 1 + (CT /100 x (TC - TNOCT)) = | 1
Expected System Energy = (EE)
|  | (EE) = (EMAX) x (KI) x (KT) x (KS) = | 0 |  | KWh
Actual System Energy Output |  |  |  |  | KWh
Percentage of Expected |  |  | #DIV/0! |  |  | >95% to Pass

## Capacity
PV Solar Site
Capacity Performance Test
Site Name:
System Designation: |  |  | Type of Inspection:
Inspection Date: |  |  | Commissioned Date:
Array must be in full sun with no shading
Module Manufacturer
Model Number
Normal Operating Cell Temperature NOCT (800W/m2 and 45.7oC) |  |  |  |  | (See PV Module Data Sheet)
| Power Output @ NOCT = (PNOTC) |  |  | Watts
| Power Temp. Coef. = (PMPP) |  |  | %/oC
| Total Number of Modules |  |  | Modules
System Peak DC Power Rating = (PMAX)
|  | (PMAX) = (PSTC) X (# of Modules) = | 0 |  | Watts
System De-rating Factor = (KS)
| Module mismatch |  | 0.97
| Inverter efficiency |  | 0.96
| Module soiling |  | 1
| Module nameplate tolerance |  | 0.99
| Wiring losses |  | 0.98
| Shading |  | 1
| System availability |  | 1
| Tacking efficiency |  | 1
| Age |  | 1
|  |  |  | (KS)= the product of all of the above factors = | 0.90345
Actual Irradiance during the test |  |  |  | W/m2
Actual Module Temperature during the test |  |  |  | o C
Irradiance Factor = (KI)
|  | (KI) = Actual Irradiance / 800 W/m2 = | 0
Module Cell Temperature Facture = (KT)
|  | (KT) = 1 + (CT /100 x (TC - TNOCT)) = | 1
Expected System Performance = (PE)
|  | (PE) = (PMAX) x (KI) x (KT) x (KS) = | 0 |  | Watts
Actual System Power Output |  |  |  |  | Watts
Percentage of Expected |  |  | #DIV/0!