## Sheet1
Testing and commissioning checklist for Small and Medium size Distributed Generation |  |  |  | By: | Power Systems Engineer
Inspection, Testing and Commissioning Procedures* |  |  |  | Date:
ITEM |  | TEST ACTIVITY | RESPONSIBILITY | EXPECTED RESULT | PASS/FAIL | WITNESS |  | NOTES
PRE-TEST CONDITIONS
1.1 |  | Conduct on-site job briefing to discuss the planned actions and their sequences, known hazards, personal protection equipment, etc. | ALL | All personnel briefed & signed-off
PERSONNEL
1.2 |  | Ensure DG unit is disconnected and/or not operating | PSE/Cooperative | DG unit disconnected
INSPECTION PROCEDURES
NOTE: | These inspection procedures are not intended to relieve the Interconnecting party/member-consumer from complying with all state-wide, local and other applicable inspection requirements imposed by any duly-constituted regulatory authority .
2.1 |  | Verify local inspector requirements have been met | PSE/Cooperative | Compliance with local inspection requirements
Documentation to be supplied by the interconnecting member-consumer * System maps and drawing with information * PV panels and Inverters datasheets and manuals * Other supporting documents for system installation (e.g., Energy storage datasheet)
2.2 |  | Inspect utility service to the member-consumer's site. Note transformer size and the settings of near-by voltage regulation devices | PSE/Cooperative | Compliance with NESC
Adequately sized transformer
2.3 |  | The inspect of the interconnecting member-consumers' installation and facilities to ensure what has been installed in the field matches the documentation supplied to the utility. | PSE/Cooperative | All installed facilities match supplied documentation
Interconnecting
Customer
a. Inspect DG unit (e.g., PV panel array) and wiring (if readily accessible)
b. If inverter based DG, inspect inverters (if readily accessible) and record any status lights or display messages
1. Inverter settings (If inverter based DG) i. Modes of operation (default unity PF/fixed PF/ Volt-Var/ Volt-Watt) ii. VRT/HRT settings
2. Status Lights
3. Display messages
4. Other
c. Inspect the DG system's main service panel and note circuit prime-mover (PV array, wind turbine, ...) is feeding into and rating of overcurrent protective device
d. Inspect sub-panel from primemover (PV array, wind turbine, ...) and note circuit(s) PV array is feeding into and rating of overcurrent protective device
e. Inspect all grounding
f. Inspect AC disconnects, record ratings and verify operability
2.4 |  | Review programmed inverter field-settings for interoperablity, voltage, and frequency trip points and confirm compliance with IEEE Std. 1547-2018/1547.1 | PSE/Cooperative | Settings compliant with IEEE1547-2018 and 1547.1 The proper CATEGORY for small DG according to the standard is category (I)
a. Interoperibility testing from the most recent IEEE 1547-2018
1.Information to be exchanged (nameplate, configuration, monitoring, management)
2. The used communication protocol and performance
Category II might not be needed for Small size but most likely for medium size DGs
[8 empty] | Category I |  |  |  | Category II
|  | b. Voltage and frequency trip settings. Check compliance with IEEE 1547-2018/.1 | [5 empty] | Voltage(%) | Frequency (Hz) | ClearingTime (sec) |  | Voltage(%) | Frequency (Hz) | ClearingTime (sec)
|  | 1. Over-voltage #2 setting and trip time | [5 empty] | 120% | - | 0.16 |  | 120% | - | 0.16
|  | 2. Over-voltage #1 setting and trip time | [5 empty] | 110% | - | 2 |  | 110% | - | 2
|  | 3. Under-voltage #1 setting and trip time | [5 empty] | 70% | - | 2 |  | 70% | - | 10
|  | 4. Under-voltage #2 setting and trip time | [5 empty] | 45% | - | 0.16 |  | 45% | - | 0.16
|  | 5. Over-frequency #2 setting and trip time | [5 empty] | - | 62 | 0.16 |  | - | 62 | 0.16
|  | 6. Over-frequency #1 setting and trip time | [5 empty] | - | 61.2 | 300 |  | - | 61.2 | 300
|  | 7. Under-frequency #1 setting and trip time | [5 empty] | - | 58.5 | 300 |  | - | 58.5 | 300
|  | 8. Under-frequency #2 setting and trip time | [5 empty] | - | 56.5 | 0.16 |  | - | 56.5 | 0.16
TESTING PROCEDURES
NOTE: |  | It is recommended to follow IEEE 1547.1-2020
3.1 |  | Verify DG unit is disconnected and/or not operating | PSE/Cooperative | DG unit disconnected
3.2 |  | Measure and record voltage at the meter, main panel and the primemover (PV sub-panel with the PV array or WT, battery cells, etc) disconnected and/or not operating | PSE/Cooperative | It can be 120/240V or another voltage service
a. Voltage measured at meter
|  | 1. L1 to L2 |  | 95-105% of Line Voltage
|  | 2. L1 to Neutral |  | 95-105% of Phase Voltage
|  | 3. L2 to Neutral |  | 95-105% of Phase Voltage
b. Voltage measured at main panel
|  | 1. L1 to L2 |  | 91.7-105% of Line Voltage
|  | 2. L1 to Neutral |  | 91.7-105% of Phase Voltage
|  | 3. L2 to Neutral |  | 91.7-105% of Phase Voltage
c. Voltage measured at PV sub-panel
|  | 1. L1 to L2 |  | 91.7-105% of Line Voltage
|  | 2. L1 to Neutral |  | 91.7-105% of Phase Voltage
|  | 3. L2 to Neutral |  | 91.7-105% of Phase Voltage
3.3 |  | Establish AC voltage to the primemover (PV array/WT/battery cells) and record time until the inverters begin outputting power. | PSE/Cooperative | Minimum 5 minute delay before inverters output power |  |  |  | Connect an Ammeter in the PV AC circuit(s)
Connect an ammeter in the DG unit AC circuit(s) to determine when the inverters begin outputting power
3.4 |  | Measure and record voltage at the meter, main panel and the | PSE/Cooperative | It can be 120/240V or another voltage service
DG unit output AC power (PV array/WT/battery outputting power)
a. Voltage measured at meter
|  | 1. L1 to L2 |  | 95-105% of Line Voltage
|  | 2. L1 to Neutral |  | 95-105% of Phase Voltage
|  | 3. L2 to Neutral |  | 95-105% of Phase Voltage
b. Voltage measured at main panel
|  | 1. L1 to L2 |  | 91.7-105% of Line Voltage
|  | 2. L1 to Neutral |  | 91.7-105% of Phase Voltage
|  | 3. L2 to Neutral |  | 91.7-105% of Phase Voltage
c. Voltage measured at sub-panel
|  | 1. L1 to L2 |  | 91.7-105% of Line Voltage
|  | 2. L1 to Neutral |  | 91.7-105% of Phase Voltage
|  | 3. L2 to Neutral |  | 91.7-105% of Phase Voltage
3.5 |  | Measure and record amperage in each DG unit (PV/WT/battery) AC circuit | PSE/Cooperative | Current up to the rated capacity present
a. Amperage measured at main service panel
b. Amperage measured at PV sub-panel
3.6 |  | Optional for inverters certified to meet UL 1741: |  | Compliance with IEEE Std. 1547-2018 & IEEE 1547.1
|  | a. Measure and record individual current harmonics and total harmonic distortion | PSE/Cooperative
|  | b. Measure and record DC component (frequency < 1 Hz) of current | PSE/Cooperative
|  | c. Require interconnecting customer to perform field tests verifying over/under voltage and frequency trip points and times | Interconnecting
Taken directly from the most recent IEEE 1547 version
3.7 |  | Conduct a "cease-to-energize" test | PSE/Cooperative | Compliance with IEEE Std. 1547-2018 & IEEE 1547.1 |  |  | following IEEE 1547.1-2020, identify the category, then the sequancy of testing conditions
Connect an Mutimeter in the DG unit AC circuit(s) to determine when the inverters stop/begin outputting power
a. Verify DG unit is operating and connected in parallel with utility source.
b. Remove utility source by opening a main breaker or opening a fuse. Ideally the device used to disconnect the utility source will still allow the residence loads to be connected on the DG unit side of the open
|  | c. Record the time for the DC side and inverters to automatically stop outputting power. |  | Output ceases within the time specified in the tables ® |  |  |  | Connect an Ammeter in the DG unit's AC circuit(s)
d. Observe the status of the inverters and record any status lights or display messages
1. Status Lights
2. Display messages
3. Other
|  | e. Re-establish AC voltage to the PV array/WT and record time until the inverters begin outputting power again. |  | Minimum 5 minute delay before inverters output power |  |  |  | Connect an Ammeter in the PV AC circuit(s)
COMMENTS
WITNESSED BY: |  |  |  |  | DATE:
: Cooperative
: Cooperative
: Cooperative
: Power System Engineering
: Interconnecting Customer
: __________________
: __________________
: __________________
ENERGY STORAGE TESTING RECOMMENDIATIONS & STANDARDS
NOTES: |  | It is recommended to follow some of the following as the co-op agrees: * Work with the co-op and the fire department to check the recommended location to install BESS if it is at a commercial facility * Work with the co-op to identify the recommended location to install BESS if it is at a residential member-consumer
3.8 |  | List of the complied standards for the Installation of stationary energy storage systems (ESS)
a. NFPA 1-18 Fire Code: chapter 52 includes requirements related to ESS
b. NFPA 855: Standard for the Installation of Stationary Energy Storage Systems
c. UL 9540: Energy Storage Systems and Equipment--Product safety standard for an ESS.
d. UL 1973: Batteries for Use in Light Electric Rail (LER) and Stationary Applications
e. NFPA 5000-2018: Maybe needed for things related to building construction and saftey codes
3.9 |  | List of tests to be conducted at the DG unit if it has ESS
a. simple Fail Safe mechanism (Transfer switch or relay) to prevent back-feed when there is an outage.
*DISCLAIMER
Utility's observation, review, inspection or testing shall be construed neither as an endorsement or confirmation of any aspect,
feature, element, or condition of the Generation Facility or Interconnection Customer's protective equipment or the operation
thereof, nor as a warranty as to the fitness, safety, desirability, or reliability of same.
Note on G62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These should be in p.u scale ANSI limits & IEEE 1547-2018 catagory XXX