## Blank
PV Solar Site
Commissioning Checklist
Site Name:
System Designation: |  |  | Inverter Type:
Commissioned Date: |  |  | Inverter SN:
| Safety |  |  |  | Check | Note | Photo
1 | AC & DC disconnects are in the open position.
2 | All combiner fuses holders are open.
3 | No voltage is present at either the AC or DC Disconnects.
4 | If disconnects are not in sight during testing use LOTO.
Plan Review
5 | Review "As Built" Plan changes.
6 | Equipment locations, model #s and specifications as per Plan.
7 | OCP amperage and voltage as per Plan.
8 | Conduit sizes and materials as per Plan.
9 | Current carrying conductor size and type as per Plan.
10 | Grounding and Bonding Conductor - Size and Type as per Plan.
11 | Equipment and Conduits Grounded or Bonded as per Plan.
Inverter Output and AC Disconnects
12 | Net Metered OCP is installed in the correct panel location and is properly labeled.
13 | All Code and PSS required labels are on the AC disconnect cover.
14 | AC disconnect terminations have been torqued and labeled.
15 | The AC disconnect is wired as per Plan.
16 | The AC disconnect is securely attached and neat.
Inverter
17 | The Inverter is properly sited and secured with all manufacture's required clearances.
18 | Isolation transformer terminations are as per manufacture's instructions and torqued.
19 | AC & DC terminations are as per manufacture's instructions, torqued and labeled.
20 | Visually inspect the inverter enclosure for signs of damage in shipping or siting and that all doors open freely.
21 | Visually inspect the interior of the inverter and check for loose sub-assemblies and connections.
22 | Inverter ventilation fan moves freely and filters are in-place.
23 | All Code and PSS required labels are on the inverter doors.
24 | Bender RCMS Unit and combiner power supply is properly installed as per PSS's installation instructions.
| PV Output to Inverter |  |  |  | Check | Note | Photo
25 | Junction box terminations are torqued, cables are labeled and properly grounded.
26 | Cables routed through conduit bodies are neat and not damaging Cable insulation.
27 | Expansion joints are installed as per manufacture's instructions and per Plans.
28 | Conduit runs are per Plan, neat, supported properly and the conduit fittings are tight.
29 | The DC disconnect is securely attached and neat.
30 | The DC disconnect is wired as per manufacture's and PSS's instructions.
31 | DC disconnect terminations have been torqued and labeled.
32 | All Code and PSS required labels are on the DC disconnect cover.
PV Array
33 | Racking is complete and installed as per the manufacturer's instructions.
34 | The module's nameplate specification are as per the Plans.
35 | Modules are installed and mounted as per the manufacture's instructions.
36 | There are no damaged or misaligned modules in the array.
37 | PV connectors are installed as per the manufacture's instructions and fully engaged.
38 | PV Wiring is properly supported, neat and there are no point where the insulation could become damaged.
39 | Array combiners are terminated as per Plans and are neat.
40 | Combiner terminations have been torqued and labeled.
41 | All Code and PSS required labels are on the combiner cover.
42 | Review the String Open Circuit Voltage and Short Circuit Amperage Test Results.
43 | Review DC Array Megger Test results.
Inverter Start-up
44 | Close the inverter AC disconnects and power-up the inverter AC side, record the line voltages.
45 | Turn on the inverter and test all safety interlocks (door switches, Bender, Anti-Islanding, etc).
46 | Close all combiner fuse holders and any manual disconnects
47 | Confirm DC voltage and polarity at the DC disconnect and at the inverter.
48 | Confirm the AC and DC Surge Protection is operational.
49 | Close the inverter DC disconnects and put the inverter on line.
50 | Confirm inverter display voltages and check inverter output.
51 | Complete Performance Testing
| Monitoring Equipment |  |  |  | Check | Note | Photo
52 | Weather Station equipment is installated and wired as per the manufacture's instructions.
53 | Power Monitoring equipment is installated and wired as per the manufacture's instructions.
54 | Monitoiring from the inverter and the Gateway is complete and operational.
Inspection Notes
Readings
Irradiance - Watt/m2: |  |  | Ambient Temp. 0C.:
Readings from the Inverter Display |  |  | Field Measured Readings
AC Line Voltage |  |  | AC Line Voltage
| Phase A to Grd: |  |  | Phase A to Grd:
| Phase B to Grd: |  |  | Phase B to Grd:
| Phase C to Grd: |  |  | Phase C to Grd:
AC Line Current |  |  | AC Line Current
| Phase A: |  |  | Phase A:
| Phase B: |  |  | Phase B:
| Phase C: |  |  | Phase C:
AC Line KW |  |  | AC Line KW
DC Input Voltage: |  |  | DC Input Voltage:
DC Input Current: |  |  | DC Input Current:
Control Power:
Commissioner
Annual
Semi-annual
|  | Dick Crafts |  |  |  |  | Yes
|  | Thomas Golder |  |  |  |  | No
N/A
William Woods